## Building 2 - Measures
Requirements: | Full wireless LAN (Wi-Fi) coverage
outlet ratio | 2 | / | 10 | m2
Floor | 0 |  |  |  |  | Floor | 1
Rooms | 11 |  |  |  |  | Rooms | 15
Ceiling | 4 | m |  |  |  | Ceiling | 3 | m
Length | 41 | m |  |  |  | Length | 41 | m
Width | 20 | m |  |  |  | Width | 20 | m
Floor Area | 820 | m2 |  |  |  | Floor Area | 820 | m2
Util Floor Area | 439.3976 | m2 |  |  |  | Util Floor Area | 454.0145 | m2
Room | Length (m) | Width(m) | Area (m2) | Type | Network Outlets | Room | Length (m) | Width(m) | Area (m2) | Type | Network Outlets
2.0.1 | 3.4 | 5.98 | 20 |  | 2 | 2.1.1 | 4.07 | 7.27 | 29.5889 |  | 6
2.0.2 | 3.4 | 5.98 | 20 |  | 2 | 2.1.2 | 3.78 | 7.27 | 27.4806 |  | 6
2.0.3 | 3.4 | 5.98 | 20 |  | 2 | 2.1.3 | 3.78 | 7.27 | 27.4806 |  | 6
2.0.4 | 3.4 | 5.98 | 20 |  | 2 | 2.1.4 | 3.78 | 7.27 | 27.4806 |  | 6
2.0.5 | 5.1 | 8.83 | 45 |  | 10 | 2.1.5 | 3.78 | 7.27 | 27.4806 |  | 6
2.0.6 | 9.97 | 11.34 | 113 |  | 5 | 2.1.6 | 7.26 | 4.65 | 33.759 |  | 8
2.0.7 | 9.97 | 11.34 | 113 |  | 5 | 2.1.7 | 7.26 | 4.65 | 33.759 |  | 8
2.0.8 | 3.42 | 8.79 | 30 |  | 6 | 2.1.8 | 7.26 | 4.65 | 33.759 |  | 8
2.0.9 | 3.42 | 8.79 | 30 |  | 6 | 2.1.9 | 7.26 | 4.65 | 33.759 |  | 8
2.0.10 | 4.72 | 3.35 | 15.812 |  | 2 | 2.1.10 | 7.26 | 4.65 | 33.759 |  | 8
2.0.11 | 3.42 | 3.68 | 12.5856 | storage | 0 | 2.1.11 | 7.26 | 4.37 | 31.7262 |  | 8
Wi-Fi AP | N/A | N/A | 0 |  | 1 | 2.1.12 | 7.26 | 1.75 | 12.705 | storage | 0
| N/A | N/A | 0 |  | 0 | 2.1.13 | 7.26 | 4.65 | 33.759 |  | 8
|  |  |  | Total | 43 | 2.1.14 | 7.26 | 4.65 | 33.759 |  | 8
[6 empty] | 2.1.15 | 7.26 | 4.65 | 33.759 |  | 8
[6 empty] | Wi-Fi AP | N/A | N/A | 0 |  | 1
[10 empty] | Total | 103

## Building 2 - Cables
Requirements: | Full wireless LAN (Wi-Fi) coverage
minimum outlets per work area |  |  | 2
outlet ratio | 2 | / | 10 | m2
Floor | 0 | [6 empty] | Floor | 1
Rooms | 12 | [6 empty] | Rooms | 13
Ceiling | 4 | m | [5 empty] | Ceiling | 3 | m
Length | 20 | m | [5 empty] | Length | 20 | m
Width | 20 | m | [5 empty] | Width | 20 | m
Floor Area | 400 | m2 | [5 empty] | Floor Area | 400 | m2
Util Floor Area | 72.83 | m2 | [5 empty] | Util Floor Area | 112.18 | m2
Cable | [7 empty] | Cable
From | To | Type | Lenght 1 | Lenght 2 | Lenght 3 | Lenght 4 | Total | From | To | Type | Lenght 1 | Lenght 2 | Lenght 3 | Lenght 4 | Total
IC | HC Floor 0 | Fiber | 1 |  |  |  | 1 | IC | HC Floor 1 | Fiber | 1.5 |  |  |  | 1.5
HC Floor 0 | CP 2.0.5 | Fiber | 37.37 |  |  |  | 37.37 | HC Floor 1 | CP 2.1.5 | Fiber | 38.44 | 5 |  |  | 43.44
[8 empty] | HC Floor 1 | CP 2.1.13 | Fiber | 38.44 | 18.32 | 11.27 |  | 68.03
HC Floor 0 | R2.0.10 O1 | CAT 7 | 4.2 | 1.08 | 1 |  | 6.28
HC Floor 0 | R2.0.10 O2 | CAT 7 | 6.34 | 1.08 | 1 |  | 8.42 | HC Floor 1 | R2.1.11 O1 | CAT 7 | 2.45 | 1 | 1.02 |  | 4.47
HC Floor 0 | R2.0.09 O1 | CAT 7 | 2.04 | 1.67 | 1 |  | 4.71 | HC Floor 1 | R2.1.11 O2 | CAT 7 | 2.45 | 1 | 1.02 |  | 4.47
HC Floor 0 | R2.0.09 O2 | CAT 7 | 2.04 | 1.67 | 1 |  | 4.71 | HC Floor 1 | R2.1.11 O3 | CAT 7 | 2.45 | 2.47 | 1.02 |  | 5.94
HC Floor 0 | R2.0.09 O3 | CAT 7 | 2.04 | 4.13 | 1 |  | 7.17 | HC Floor 1 | R2.1.11 O4 | CAT 7 | 2.45 | 2.47 | 1.02 |  | 5.94
HC Floor 0 | R2.0.09 O4 | CAT 7 | 2.04 | 4.13 | 1 |  | 7.17 | HC Floor 1 | R2.1.11 O5 | CAT 7 | 2.45 | 4.25 | 1.02 |  | 7.72
HC Floor 0 | R2.0.09 O5 | CAT 7 | 2.04 | 6.9 | 1 |  | 9.94 | HC Floor 1 | R2.1.11 O6 | CAT 7 | 2.45 | 4.25 | 1.02 |  | 7.72
HC Floor 0 | R2.0.09 O6 | CAT 7 | 2.04 | 6.9 | 1 |  | 9.94 | HC Floor 1 | R2.1.11 O7 | CAT 7 | 2.45 | 5.91 | 1.02 |  | 9.38
HC Floor 0 | R2.0.08 O1 | CAT 7 | 5.84 | 1.61 | 1 |  | 8.45 | HC Floor 1 | R2.1.11 O8 | CAT 7 | 2.45 | 5.91 | 1.02 |  | 9.38
HC Floor 0 | R2.0.08 O2 | CAT 7 | 5.84 | 1.61 | 1 |  | 8.45 | HC Floor 1 | R2.1.10 O1 | CAT 7 | 7.1 | 0.48 | 1.06 |  | 8.64
HC Floor 0 | R2.0.08 O3 | CAT 7 | 5.84 | 4.08 | 1 |  | 10.92 | HC Floor 1 | R2.1.10 O2 | CAT 7 | 7.1 | 0.48 | 1.06 |  | 8.64
HC Floor 0 | R2.0.08 O4 | CAT 7 | 5.84 | 4.08 | 1 |  | 10.92 | HC Floor 1 | R2.1.10 O3 | CAT 7 | 7.1 | 2.37 | 1.06 |  | 10.53
HC Floor 0 | R2.0.08 O5 | CAT 7 | 5.84 | 6.77 | 1 |  | 13.61 | HC Floor 1 | R2.1.10 O4 | CAT 7 | 7.1 | 2.37 | 1.06 |  | 10.53
HC Floor 0 | R2.0.08 O6 | CAT 7 | 5.84 | 6.77 | 1 |  | 13.61 | HC Floor 1 | R2.1.10 O5 | CAT 7 | 7.1 | 4.2 | 1.06 |  | 12.36
HC Floor 0 | R2.0.07 O1 | CAT 7 | 8.13 |  |  |  | 8.13 | HC Floor 1 | R2.1.10 O6 | CAT 7 | 7.1 | 4.2 | 1.06 |  | 12.36
HC Floor 0 | R2.0.07 O2 | CAT 7 | 10.17 |  |  |  | 10.17 | HC Floor 1 | R2.1.10 O7 | CAT 7 | 7.1 | 6.1 | 1.06 |  | 14.26
HC Floor 0 | R2.0.07 O3 | CAT 7 | 12.28 |  |  |  | 12.28 | HC Floor 1 | R2.1.10 O8 | CAT 7 | 7.1 | 6.1 | 1.06 |  | 14.26
HC Floor 0 | R2.0.07 O4 | CAT 7 | 14.38 |  |  |  | 14.38 | HC Floor 1 | R2.1.09 O1 | CAT 7 | 11.82 | 0.46 | 1.07 |  | 13.35
HC Floor 0 | R2.0.07 O5 | CAT 7 | 16.48 |  |  |  | 16.48 | HC Floor 1 | R2.1.09 O2 | CAT 7 | 11.82 | 0.46 | 1.07 |  | 13.35
HC Floor 0 | R2.0.06 O1 | CAT 7 | 18.7 |  |  |  | 18.7 | HC Floor 1 | R2.1.09 O3 | CAT 7 | 11.82 | 2.37 | 1.07 |  | 15.26
HC Floor 0 | R2.0.06 O2 | CAT 7 | 20.81 |  |  |  | 20.81 | HC Floor 1 | R2.1.09 O4 | CAT 7 | 11.82 | 2.37 | 1.07 |  | 15.26
HC Floor 0 | R2.0.06 O3 | CAT 7 | 22.9 |  |  |  | 22.9 | HC Floor 1 | R2.1.09 O5 | CAT 7 | 11.82 | 4.19 | 1.07 |  | 17.08
HC Floor 0 | R2.0.06 O4 | CAT 7 | 25.01 |  |  |  | 25.01 | HC Floor 1 | R2.1.09 O6 | CAT 7 | 11.82 | 4.19 | 1.07 |  | 17.08
HC Floor 0 | R2.0.06 O5 | CAT 7 | 27.15 |  |  |  | 27.15 | HC Floor 1 | R2.1.09 O7 | CAT 7 | 11.82 | 5.87 | 1.07 |  | 18.76
HC Floor 0 | O Wi-Fi | CAT 7 | 18.32 | 11.9 |  |  | 30.22 | HC Floor 1 | R2.1.09 O8 | CAT 7 | 11.82 | 5.87 | 1.07 |  | 18.76
CP 2.0.5 | R2.0.05 O1 | CAT 7 | 2 | 1.24 | 0.8 |  | 4.04 | HC Floor 1 | R2.1.08 O1 | CAT 7 | 16.51 | 0.5 | 1.04 |  | 18.05
CP 2.0.5 | R2.0.05 O2 | CAT 7 | 2 | 1.24 | 0.8 |  | 4.04 | HC Floor 1 | R2.1.08 O2 | CAT 7 | 16.51 | 0.5 | 1.04 |  | 18.05
CP 2.0.5 | R2.0.05 O3 | CAT 7 | 2 | 2.88 | 0.8 |  | 5.68 | HC Floor 1 | R2.1.08 O3 | CAT 7 | 16.51 | 2.4 | 1.04 |  | 19.95
CP 2.0.5 | R2.0.05 O4 | CAT 7 | 2 | 2.88 | 0.8 |  | 5.68 | HC Floor 1 | R2.1.08 O4 | CAT 7 | 16.51 | 2.4 | 1.04 |  | 19.95
CP 2.0.5 | R2.0.05 O5 | CAT 7 | 2 | 4.61 | 0.8 |  | 7.41 | HC Floor 1 | R2.1.08 O5 | CAT 7 | 16.51 | 4.18 | 1.04 |  | 21.73
CP 2.0.5 | R2.0.05 O6 | CAT 7 | 2 | 4.61 | 0.8 |  | 7.41 | HC Floor 1 | R2.1.08 O6 | CAT 7 | 16.51 | 4.18 | 1.04 |  | 21.73
CP 2.0.5 | R2.0.05 O7 | CAT 7 | 2 | 6.22 | 0.8 |  | 9.02 | HC Floor 1 | R2.1.08 O7 | CAT 7 | 16.51 | 5.89 | 1.04 |  | 23.44
CP 2.0.5 | R2.0.05 O8 | CAT 7 | 2 | 6.22 | 0.8 |  | 9.02 | HC Floor 1 | R2.1.08 O8 | CAT 7 | 16.51 | 5.89 | 1.04 |  | 23.44
CP 2.0.5 | R2.0.05 O9 | CAT 7 | 2 | 7.77 | 0.8 |  | 10.57 | HC Floor 1 | O Wi-Fi | CAT 7 | 16.51 | 7.33 | 1.04 |  | 24.88
CP 2.0.5 | R2.0.05 O10 | CAT 7 | 2 | 7.77 | 0.8 |  | 10.57 | HC Floor 1 | R2.1.07 O1 | CAT 7 | 21.39 | 0.67 | 0.98 |  | 23.04
CP 2.0.5 | R2.0.4 O1 | CAT 7 | 6.07 | 3.18 | 0.7 |  | 9.95 | HC Floor 1 | R2.1.07 O2 | CAT 7 | 21.39 | 0.67 | 0.98 |  | 23.04
CP 2.0.5 | R2.0.4 O2 | CAT 7 | 6.07 | 3.18 | 0.7 |  | 9.95 | HC Floor 1 | R2.1.07 O3 | CAT 7 | 21.39 | 2.51 | 0.98 |  | 24.88
CP 2.0.5 | R2.0.3 O1 | CAT 7 | 9.43 | 3.25 | 0.7 |  | 13.38 | HC Floor 1 | R2.1.07 O4 | CAT 7 | 21.39 | 2.51 | 0.98 |  | 24.88
CP 2.0.5 | R2.0.3 O2 | CAT 7 | 9.43 | 3.25 | 0.7 |  | 13.38 | HC Floor 1 | R2.1.07 O5 | CAT 7 | 21.39 | 4.34 | 0.98 |  | 26.71
CP 2.0.5 | R2.0.2 O1 | CAT 7 | 13.47 | 3.25 | 0.7 |  | 17.42 | HC Floor 1 | R2.1.07 O6 | CAT 7 | 21.39 | 4.34 | 0.98 |  | 26.71
CP 2.0.5 | R2.0.2 O2 | CAT 7 | 13.47 | 3.25 | 0.7 |  | 17.42 | HC Floor 1 | R2.1.07 O7 | CAT 7 | 21.39 | 5.91 | 0.98 |  | 28.28
CP 2.0.5 | R2.0.1 O1 | CAT 7 | 17.15 | 3.25 | 0.7 |  | 21.1 | HC Floor 1 | R2.1.07 O8 | CAT 7 | 21.39 | 5.91 | 0.98 |  | 28.28
CP 2.0.5 | R2.0.1 O2 | CAT 7 | 17.15 | 3.25 | 0.7 |  | 21.1 | HC Floor 1 | R2.1.06 O1 | CAT 7 | 26.13 | 0.69 | 1.1 |  | 27.92
[8 empty] | HC Floor 1 | R2.1.06 O2 | CAT 7 | 26.13 | 0.69 | 1.1 |  | 27.92
[8 empty] | HC Floor 1 | R2.1.06 O3 | CAT 7 | 26.13 | 2.57 | 1.1 |  | 29.8
[7 empty] | Total | HC Floor 1 | R2.1.06 O4 | CAT 7 | 26.13 | 2.57 | 1.1 |  | 29.8
[6 empty] | Fiber | 38.37 | HC Floor 1 | R2.1.06 O5 | CAT 7 | 26.13 | 4.36 | 1.1 |  | 31.59
[6 empty] | CAT 7 | 527.67 | HC Floor 1 | R2.1.06 O6 | CAT 7 | 26.13 | 4.36 | 1.1 |  | 31.59
[8 empty] | HC Floor 1 | R2.1.06 O7 | CAT 7 | 26.13 | 6.04 | 1.1 |  | 33.27
[8 empty] | CP 2.1.5 | R2.1.05 O1 | CAT 7 | 1 | 1.24 | 1 |  | 3.24
[8 empty] | CP 2.1.5 | R2.1.05 O2 | CAT 7 | 1 | 1.24 | 1 |  | 3.24
[8 empty] | CP 2.1.5 | R2.1.05 O3 | CAT 7 | 1 | 3.22 | 1 |  | 5.22
[8 empty] | CP 2.1.5 | R2.1.05 O4 | CAT 7 | 1 | 3.22 | 1 |  | 5.22
[8 empty] | CP 2.1.5 | R2.1.05 O5 | CAT 7 | 1 | 5.36 | 1 |  | 7.36
[8 empty] | CP 2.1.5 | R2.1.05 O6 | CAT 7 | 1 | 5.36 | 1 |  | 7.36
[8 empty] | CP 2.1.5 | R2.1.04 O1 | CAT 7 | 4.62 | 1.27 | 1 |  | 6.89
[8 empty] | CP 2.1.5 | R2.1.04 O2 | CAT 7 | 4.62 | 1.27 | 1 |  | 6.89
[8 empty] | CP 2.1.5 | R2.1.04 O3 | CAT 7 | 4.62 | 3.39 | 1 |  | 9.01
[8 empty] | CP 2.1.5 | R2.1.04 O4 | CAT 7 | 4.62 | 3.39 | 1 |  | 9.01
[8 empty] | CP 2.1.5 | R2.1.04 O5 | CAT 7 | 4.62 | 5.48 | 1 |  | 11.1
[8 empty] | CP 2.1.5 | R2.1.04 O6 | CAT 7 | 4.62 | 5.48 | 1 |  | 11.1
[8 empty] | CP 2.1.5 | R2.1.03 O1 | CAT 7 | 8.5 | 1.19 | 1 |  | 10.69
[8 empty] | CP 2.1.5 | R2.1.03 O2 | CAT 7 | 8.5 | 1.19 | 1 |  | 10.69
[8 empty] | CP 2.1.5 | R2.1.03 O3 | CAT 7 | 8.5 | 3.21 | 1 |  | 12.71
[8 empty] | CP 2.1.5 | R2.1.03 O4 | CAT 7 | 8.5 | 3.21 | 1 |  | 12.71
[8 empty] | CP 2.1.5 | R2.1.03 O5 | CAT 7 | 8.5 | 5.64 | 1 |  | 15.14
[8 empty] | CP 2.1.5 | R2.1.03 O6 | CAT 7 | 8.5 | 5.64 | 1 |  | 15.14
[8 empty] | CP 2.1.5 | R2.1.02 O1 | CAT 7 | 12.27 | 1.09 | 1 |  | 14.36
[8 empty] | CP 2.1.5 | R2.1.02 O2 | CAT 7 | 12.27 | 1.09 | 1 |  | 14.36
[8 empty] | CP 2.1.5 | R2.1.02 O3 | CAT 7 | 12.27 | 3.29 | 1 |  | 16.56
[8 empty] | CP 2.1.5 | R2.1.02 O4 | CAT 7 | 12.27 | 3.29 | 1 |  | 16.56
[8 empty] | CP 2.1.5 | R2.1.02 O5 | CAT 7 | 12.27 | 5.85 | 1 |  | 19.12
[8 empty] | CP 2.1.5 | R2.1.02 O6 | CAT 7 | 12.27 | 5.85 | 1 |  | 19.12
[8 empty] | CP 2.1.5 | R2.1.01 O1 | CAT 7 | 16.53 | 1.07 | 1 |  | 18.6
[8 empty] | CP 2.1.5 | R2.1.01 O2 | CAT 7 | 16.53 | 1.07 | 1 |  | 18.6
[8 empty] | CP 2.1.5 | R2.1.01 O3 | CAT 7 | 16.53 | 3.38 | 1 |  | 20.91
[8 empty] | CP 2.1.5 | R2.1.01 O4 | CAT 7 | 16.53 | 3.38 | 1 |  | 20.91
[8 empty] | CP 2.1.5 | R2.1.01 O5 | CAT 7 | 16.53 | 5.73 | 1 |  | 23.26
[8 empty] | CP 2.1.5 | R2.1.01 O6 | CAT 7 | 16.53 | 5.73 | 1 |  | 23.26
[8 empty] | CP 2.1.13 | R2.1.13 O1 | CAT 7 | 0.78 | 1 |  |  | 1.78
[8 empty] | CP 2.1.13 | R2.1.13 O2 | CAT 7 | 0.78 | 1 |  |  | 1.78
[8 empty] | CP 2.1.13 | R2.1.13 O3 | CAT 7 | 2.29 | 1 |  |  | 3.29
[8 empty] | CP 2.1.13 | R2.1.13 O4 | CAT 7 | 2.29 | 1 |  |  | 3.29
[8 empty] | CP 2.1.13 | R2.1.13 O5 | CAT 7 | 4.1 | 1 |  |  | 5.1
[8 empty] | CP 2.1.13 | R2.1.13 O6 | CAT 7 | 4.1 | 1 |  |  | 5.1
[8 empty] | CP 2.1.13 | R2.1.13 O7 | CAT 7 | 6.03 | 1 |  |  | 7.03
[8 empty] | CP 2.1.13 | R2.1.13 O8 | CAT 7 | 6.03 | 1 |  |  | 7.03
[8 empty] | CP 2.1.13 | R2.1.14 O1 | CAT 7 | 4.45 | 0.65 | 1 |  | 6.1
[8 empty] | CP 2.1.13 | R2.1.14 O2 | CAT 7 | 4.45 | 0.65 | 1 |  | 6.1
[8 empty] | CP 2.1.13 | R2.1.14 O3 | CAT 7 | 4.45 | 2.22 | 1 |  | 7.67
[8 empty] | CP 2.1.13 | R2.1.14 O4 | CAT 7 | 4.45 | 2.22 | 1 |  | 7.67
[8 empty] | CP 2.1.13 | R2.1.14 O5 | CAT 7 | 4.45 | 3.99 | 1 |  | 9.44
[8 empty] | CP 2.1.13 | R2.1.14 O6 | CAT 7 | 4.45 | 3.99 | 1 |  | 9.44
[8 empty] | CP 2.1.13 | R2.1.14 O7 | CAT 7 | 4.45 | 5.92 | 1 |  | 11.37
[8 empty] | CP 2.1.13 | R2.1.14 O8 | CAT 7 | 4.45 | 5.92 | 1 |  | 11.37
[8 empty] | CP 2.1.13 | R2.1.15 O1 | CAT 7 | 9.33 | 0.72 | 1 |  | 11.05
[8 empty] | CP 2.1.13 | R2.1.15 O2 | CAT 7 | 9.33 | 0.72 | 1 |  | 11.05
[8 empty] | CP 2.1.13 | R2.1.15 O3 | CAT 7 | 9.33 | 2.24 | 1 |  | 12.57
[8 empty] | CP 2.1.13 | R2.1.15 O4 | CAT 7 | 9.33 | 2.24 | 1 |  | 12.57
[8 empty] | CP 2.1.13 | R2.1.15 O5 | CAT 7 | 9.33 | 4.05 | 1 |  | 14.38
[8 empty] | CP 2.1.13 | R2.1.15 O6 | CAT 7 | 9.33 | 4.05 | 1 |  | 14.38
[8 empty] | CP 2.1.13 | R2.1.15 O7 | CAT 7 | 9.33 | 5.94 | 1 |  | 16.27
[8 empty] | CP 2.1.13 | R2.1.15 O8 | CAT 7 | 9.33 | 5.94 | 1 |  | 16.27
Total
[14 empty] | Fiber | 112.97
[14 empty] | CAT 7 | 1484.87

## Building 2 - TE
TE | Designation | Outlets | Ports Fiber | U (with switch) | Overdimension U | Fiber U
HC Floor 1 | CP 2.1.5 | 30 | 0 | 1 | 1 | 0
| CP 2.1.13 | 24 | 0 | 1 | 1 | 0
| HC Floor 1 | 48 | 2 | 0 | 1 | 1
HC Floor 0 | CP 2.0.5 | 18 | 0 | 1 | 1 | 0
| HC Floor 0 | 25 | 2 | 1 | 1 | 1
IC | IC | 0 | 2 | 0 | 1 | 1
Patch Panels
Designation | 24-Port Copper | 48-Port Copper | 24-Port Fibre | Racks needed(U)
IC | 1 | 0 | 1 | 4
HC 0 | 0 | 1 | 1 | 4
HC 1 | 0 | 1 | 1 | 4
CP 2.0.5 | 1 | 0 | 0 | 2
CP 2.1.5 | 0 | 1 | 0 | 2
CP 2.1.13 | 0 | 1 | 0 | 2
Total Telecommunication Enclosures(TE) |  |  | 3
Total 24-Port Copper Patch Panels |  |  | 2
Total 48-Port Copper Patch Panels |  |  | 4
Total 24-Port Fibre Patch Panels |  |  | 3